Jansen Doors

Fire Protection – Stacking door MATADOOR

Classified performance: 
EI2 90 C
Fire retardant and self-closing

Additional performance:
Durability of self-closure: C2 (10,000 load cycles)

Door leaf: 
Individual elements are connected to form a door leaf staggered system

Door leaf and lateral supports made of galvanized sheet metal

Safety device incl. fall protection according to DIN EN 12604

Dimensions :

Clear door height :

Clear door width :

Lintel height :

Control & Drive:

Fire protection drive 400V/16A with centrifugal regulator for a controlled closing speed.

(Builder-owner provided: 400 V/16A supply cable with CEE plug near the door)

Dimensions control box (WxHxD): 400 x 500 x 210 mm

VdS-tested, battery-buffered for approx. 4 hours, hold-open system with smoke switches, number according to DIBt guidelines.

Release button: 1x single button red rocker

1 x signal transmitter as combination optical/acoustic

Floor closure with self-monitoring safety strip.

Locking function and closing also in case of power failure.

Operation with a double surface-mounted push-button.

Mode of operation: Dead man

Installation method for electrical components: Plastic cable duct light grey

Reference product

Jansentore GmbH & Co. KG  -  Stacking door MATADOOR

www.jansentore.com